## Slide 1
Representative Sampling
BACWA/EBMUD Pretreatment Training
March 11, 2019
Greg V. Arthur - (510) 967-8411 - gva@gvarthur.com

## Slide 2
Self-Monitoring
Requirements
40 CFR 403.12(e)(1)

## Slide 3
40 CFR 403.12(g)(1)

## Slide 4
40 CFR 403.12(g)(1)

## Slide 5
40 CFR 403.12(g)(3)

## Slide 6
40 CFR 403.12(g)(3)

## Slide 7
Self-Monitoring
Requirements
40 CFR 403.12
The Bottom Line
Twice per year reports of
self-monitoring.
Each sample must be
representative over the
sampling day.
Sampling must be repre-
sentative of all regulated
discharges.
The sample record must be
representative over the six-
month reporting period.

## Slide 8
So …
Self-Monitoring
Complies with Federal
Regulations
If …
All samples together are representative of the flow, nature, and concentration of the discharge over the entire six-month
reporting period.
Self-Monitoring
Requirements
40 CFR 403.12

## Slide 9
The Test for
Representative Sampling
Are there enough samples taken at the right times from the right locations to be representative of the discharge over the entire six-month reporting period?

## Slide 10
Federal Minimum
Can one 24-hr comp sample be representative over a six-month reporting period?
Yes, but only if …
consistent flow and
nature
random distribution
variability only from BAT
little variability from ops

## Slide 11
Are there enough samples taken at the right times and locations to be representative of the discharge over the six-month reporting period?
Complication #1
Independent events
batch treatment
spent solutions
intermittent operations

## Slide 12
continuous treat
for metals rinses
lamella
clarifier
batch treat
for CN
spents
batch treat
for metals
spents

## Slide 13
~7 days
intermittent
batch treat
for CN
spents
batch treat
for metals
spents
lamella
clarifier
continuous treat
for metals rinses
spents spents
rinses
continuous
intermittent
sample point
How many samples are necessary to capture both independent events (continuous & 7day)?

## Slide 14
How many samples are necessary to capture both independent events (continuous & 7day)?
continuous
only
continuous
plus ~7day batch

## Slide 15
How many samples are necessary to capture both independent events (continuous & 7day)?
Runs 1 - 10
ooooo
oooooooooooooooooooooo
oo
oooooooo
oooooooooooooo
ooooo
ooooooooo
oooooooooo
oooooooo
o

## Slide 16
How many samples are necessary to capture both independent events (continuous & 7day)?
Runs 11 - 20
ooooooooooooooo
ooo
ooooooooooooooooooooooooo
ooooooooo
oooooo
oo
oooooooooooooooo
oooooooooooooooo
o
oooooo

## Slide 17
How many samples are necessary to capture both independent events (continuous & 7day)?
Runs 21 - 30
oooooo
oooooo
oo
oooooo
ooo
ooooooooo
ooooooooooo
ooooo
ooo
oooo

## Slide 18
How many samples are necessary to capture both independent events (continuous & 7day)?
Runs 31 - 40
oo
o
oo
ooooo
ooooooo
oooo
ooo
ooooo
o
oooo

## Slide 19
How many samples are necessary to capture both independent events (continuous & 7day)?
Runs 41 - 50
o
oooooooo
oooooooooooo
oooo
oooooooo
oo
ooo
ooooooooooo
ooooooooooooo
o

## Slide 20
How many samples are necessary to capture both independent events (continuous & 7day)?
Mean = 7.0 StDev = 5.4
Probability of capturing both
independent events in:
1 sample – 15%
2 samples – 20%
3 samples – 25%
6 samples – 43% (monthly)
7 samples – 50%
12 samples – 80%
20 samples – 99%

## Slide 21
How many samples are necessary to capture both independent events (continuous & 7day)?
Mean = 3.0 StDev = 2.5
Probability of capturing both
independent events in:
1 sample – 21%
2 samples – 34%
3 samples – 50%
4 samples – 66%
5 samples – 79%
6 samples – 88% (monthly)
9 samples – 99%

## Slide 22
How many samples are necessary to capture both independent events (continuous & 7day)?
An Independent Event is any significant source of variability in the discharge quality or flow
Likely significant sources
Process spent solutions
seasonal
O&M
blowdowns
Treatment batch treatment
dewatering
Discharge combined sources

## Slide 23
Are there enough samples taken at the right times and locations to be representative of the discharge over the six-month reporting period?
Complication #2
Non-random Bias
weekend operations
periodic contributions
scheduled blowdowns

## Slide 24
How many samples are necessary to capture both independent events (continuous & 7day)?
Runs Mon – Sun
Mon ooooooooooooooo
Tue ooo
Wed oooooooooooooooooo
Thu ooooooooooo
Fri ooooooo
Sat oo
Sun oooooooooooooooo
1 Mon-Fri and 1 Sat-Sun

## Slide 25
Complication #1
Independent events
test prior to discharge
sampling to cover all events
determine if on schedules
metering
equalization
Complication #2
Non-random Bias
scheduled sampling
equalization

## Slide 26
Representative Sampling
BACWA/EBMUD Pretreatment Training
March 11, 2019
Questions or Comments
Greg V. Arthur - (510) 967-8411 - gva@gvarthur.com