## Slide 1: Santa Rosa’s PFAS Sampling and Results
Robert C. Wilson
City of Santa Rosa
October 6, 2021

## Slide 2: PFAS Background Inforamtion
What are Per and Polyfluorinated Substances (PFAS) and why are they in use?

## Slide 3: What are they?
Human made chemicals that are used un manufacturing from various industries around the globe since the 1940s.
Used in
  Food containers
  Commercial household products
    Electronics
    Carpet
    Paint, sealants, and varnishes
  Personal Care Products
  Firefighting foams

## Slide 4: Why are they used?
The group of chemicals are used to make coatings and products that resist heat, oil, stains, grease, and water.
Some of the congeners are used and studied more than others.

## Slide 5: In the media

## Slide 6: ORDER WQ 2020-0015-DWQ
Signed July 9th, 2020
Required
  Complete questionnaire
  Conduct sampling and analysis for PFAS
    Report data within 30 days of receiving the analytical report
    Submit report summarizing data no later than 60 days following the receipt of the last analytical report

## Slide 8: Preparation

## Slide 9: Preparation
The City of Santa Rosa worked with Larry Walker and Associates to develop a sampling plan
Draft plan was submitted to the RWQCB for review
Addressed
  Separate spaces where only certain event activates will take place
    Eating, Staging, and Sampling
  Prohibited materials
    Water/stain/dirt resistant clothing
    Clothes recently washed with Fabric softeners
    Clothes chemically treated for insect repellant or UV Protection
    New unwashed clothing
    First-aid adhesive wrappers.

## Slide 12: Preparation (Continued)

## Slide 13: Influent Sampler

## Slide 14: Effluent Sampler

## Slide 15: Original Biosolids Sample Cup

## Slide 16: Replacement Biosolids Sample Cup

## Slide 17: Results

## Slide 18: So how did we do?
Worked with Vista laboratories (sub-contract) to analyze DI blanks to test equipment prior to sampling
  Test blanks returned non-detect results
  Required the shipment of blank water from Vista
Influent and Effluent first sampled November 2020 and Biosolids sampled December 2020
Blanks remained non-detect throughout the project

## Slide 19: Influent Sample Data
Chart: Influent Sample Date
| 44148 | 44224 | 44294 | 44392
PFBA | 5.03 | 17.5 | 6.91 | 0
PFPeA | 7.35 | 23 | 5.62 | 0
PFBS | 0 | 10.6 | 0 | 0
PFHxA | 10.9 | 33.9 | 10 | 0
PFPeS | 18.6 | 0 | 0 | 0
PFHpA | 0 | 6.34 | 0 | 0
ADONA | 0 | 8.21 | 0 | 0
PFHxS | 4.34 | 5.04 | 0 | 0
PFOA | 0 | 25.8 | 4.81 | 0
PFOS | 5.11 | 9.79 | 0 | 0
PFDA | 0 | 0 | 0 | 0
MeFOSAA | 0 | 4.65 | 0 | 0

## Slide 20: Effluent Sample Data
Chart: Effluent Sample Date
| 44148 | 44224 | 44294 | 44392
PFBA | 13.2 | 10.1 | 5.54 | 5.55
PFPeA | 23.5 | 22.3 | 10.7 | 11.8
PFBS | 9.05 | 5.49 | 8.25 | 0
PFHxA | 30.7 | 26.8 | 17.1 | 25.3
PFHpA | 0 | 4.89 | 0 | 0
PFHxS | 5.28 | 0 | 0 | 0
PFOA | 11.6 | 109 | 8.75 | 12.1
PFOSA | 7.2 | 9.27 | 17 | 0
PFOS | 6.35 | 11.1 | 5.72 | 0

## Slide 21: Dewatered Biosolids Data
Chart: Dewatered Biosolids Sample Date
| 44168 | 44224 | 44294 | 44392
PFBS | 0 | 4.61 | 3.45 | 0
PFHxA | 2.58 | 2.36 | 3.32 | 3.84
PFHxS | 0.79 | 0 | 0 | 0
PFOA | 0.91 | 1.71 | 1.24 | 1.57
PFNA | 0.534 | 0 | 0 | 0
PFOS | 20.2 | 14.5 | 20.3 | 10.4
PFDA | 3.35 | 4.78 | 3.02 | 3.38
MeFOSAA | 18.8 | 18.5 | 18.3 | 19.3
EtFOSAA | 16.6 | 17.6 | 12.3 | 13
PFUnA | 0.75 | 0.622 | 0 | 0
PFDoA | 2.37 | 2.11 | 2.98 | 2.76
PFTeDA | 0.501 | 0 | 0 | 0

## Slide 22: Biosolids Application Sites
Chart: Biosolids Application Site Monitoring Wells April and July 2021 Sampling
| MW 101 April | MW 103 April | MW 101 July | MW 103 July | MW 102 July
PFBA | 35.7 | 2.2 | 29.7 | 2.02 | 56
PFPeA | 34.9 | 0 | 22.7 | 0 | 31.4
PFBS | 490 | 19.4 | 381 | 22 | 130
PFHxA | 44.4 | 0 | 31.8 | 0 | 35.5
PFPeS | 8.9 | 3.78 | 7.64 | 2.67 | 3.79
PFHpA | 25 | 0 | 15.6 | 0 | 15.7
PFHxS | 45.3 | 18.4 | 38 | 19 | 34.7
PFOA | 58.1 | 0 | 36.9 | 0 | 80.5
PFHpS | 0 | 0 | 0 | 0 | 2.79
PFOSA | 0 | 0 | 2.11 | 0 | 0
PFOS | 10.6 | 0 | 7.84 | 0 | 41.4

## Slide 23
Chart: Biosolids Application Site Monitoring Wells April and July 2021 Sampling
| MW 101 April | MW 103 April | MW 101 July | MW 103 July | MW 102 July
PFBA | 35.7 | 2.2 | 29.7 | 2.02 | 56
PFPeA | 34.9 | 0 | 22.7 | 0 | 31.4
PFBS | 490 | 19.4 | 381 | 22 | 130
PFHxA | 44.4 | 0 | 31.8 | 0 | 35.5
PFPeS | 8.9 | 3.78 | 7.64 | 2.67 | 3.79
PFHpA | 25 | 0 | 15.6 | 0 | 15.7
PFHxS | 45.3 | 18.4 | 38 | 19 | 34.7
PFOA | 58.1 | 0 | 36.9 | 0 | 80.5
PFHpS | 0 | 0 | 0 | 0 | 2.79
PFOSA | 0 | 0 | 2.11 | 0 | 0
PFOS | 10.6 | 0 | 7.84 | 0 | 41.4

## Slide 24: Discussion
Understanding and making decisions from the data is challenging.
Influent had the most noticeable seasonal variation
As expected, the effluent had higher concentration compared to the influent
  No Total Organic Precursors (TOPs) on data set
Results for the downgradient wells show higher levels of PFAS
  The City is looking into the data and additional sampling to further the discussion.
  We are careful to interpret this data to suggest that biosolids lead to increased PFAS concentrations in groundwater.

## Slide 25: Questions?